1. HOME ASSISTANT – Teknisk systemoversikt

1.1 Integrasjoner som er aktive / i bruk

MQTT (Mosquitto Addon)

- Brukes for Shelly Pro EM50 og Shelly 1 Gen4

- Transporterer:

  - Waterflow (LPM, total liters, pulser)

  - Pumpe strømstatus (P1/P2)

  - Kontactor-styring (P2)

Shelly integrasjon (Gen4 API + MQTT)

- 1 x Shelly 1 Gen4 (flow meter)

- 1 x Shelly Pro EM50 (pump control)

Home Assistant OS Addons

- Mosquitto

- InfluxDB

- Node-RED

- Samba (hvis aktiv)

- File Editor

Supervisor / OS

- HA Core 2025.11.3

- MQTT Broker v… (samme som HA-addons)

1.2 Entities i Home Assistant (strukturert)

Sensorer – Flow

sensor.waterflow_lpm

sensor.waterflow_total_liters

Kommer fra Shelly 1 Gen4 (HRI).

Sensorer – Pumpe elektriske målinger

Fra Shelly Pro EM50:

sensor.pressure_pump_voltage

sensor.pressure_pump_current

sensor.pressure_pump_active_power

sensor.pressure_pump_energy

binary_sensor.pressure_pump_running

switch.pressure_pump_contactor  (MQTT-switch)

Virtuelle sensorer fra Node-RED → HA

- sensor.virtual_pressure (bar)

- sensor.pressure_cutin_setting

- sensor.pressure_cutout_setting

- sensor.pump_cycle_liters

- sensor.pump_cycle_runtime_seconds

- sensor.leak_score

- sensor.night_usage_liters

- sensor.forecast_daily_usage (ikke aktiv ennå)

- sensor.flow_noise_index

Input helpers

input_number.virtual_pressure_cutin

input_number.virtual_pressure_cutout

input_boolean.pump_auto_mode

input_boolean.force_pump_shutdown

Brukes til å justere cut-in/cut-out, eller aktiverer AI/NR logikk.

1.3 HA Dashboards

Øyna – Waterflow dashboard

- Flow LPM

- Total liters

- Pump cycles per day

- Pressure (virtual)

- Leak status

- Nightly usage

Øyna – Pump system

- P1/P2 strøm

- P2 running status

- Cycle analysis

- Trykkberegning

- Cut-in/out justeringer

1.4 HA Automationer (per nå)

Regel 1: begrenset bruk – nesten all logikk ligger i Node-RED.

🟧 2. NODE-RED – Teknisk systemoversikt

Node-RED er det mest avanserte laget i hele Øyna-systemet.

2.1 Hovedflows

Flow 1 – Waterflow ingest

- MQTT in → parse → store measurement in InfluxDB

- Flow LPM

- Flow total

- Timestamp adjustments

- Error handling

- Flow smoothing / denoising

Flow 2 – Pump cycle detection

- EM50 strømprofil analyseres

- Start/stopp-identifikasjon

- Cycle-time

- Liters-per-cycle (fra Sensus/HRI)

- Power-normalization

- Pump overload detection

Flow 3 – Virtual pressure model

- Beregner “virtuelt trykk” basert på:

  - liters-per-cycle

  - linear pressure drop model

  - runtime

- Oppdaterer HA sensor

- Tar hensyn til cut-in/out (justerbare i HA)

Flow 4 – Leakage detection

- Nattforbruk 02–06

- Sammenligner mot baseline

- Detekterer små og store lekkasjer

- Beregner leak_score (0–1)

- Sender varsel til HA/Telegram

- Kan aktivere “force_pump_shutdown”

Flow 5 – InfluxDB aggregator

- Følgende buckets: minute / hourly / daily

- Flow, liters, cycle_count

- Pumper runtime

- Energi (fra EM50)

Flow 6 – Pump safety logic

- Virker som en “digital failsafe” over gammelt mekanisk system

- Avslår P2 når:

  - leak_score > threshold

  - frostfare

  - for mange sykluser

  - unormalt strømforbruk

  - HA-manual shutdown aktiv

Flow 7 – MQTT command processing

- Slår av/på kontaktor i EM50

- Sikrer debounce, retry, fallback

- Logger alle pump commands

2.2 Node-RED teknologistack

- Node-RED v4.1.1 (HA addon)

- node-red-contrib-influxdb2 (v2-modus)

- node-red-contrib-home-assistant-websocket

- Standard function nodes (JS)

- Context storage for:

  - last_pump_cycle

  - baseline_night_usage

  - cycle_history

  - pressure_model_state

  - leak_history

🟩 3. INFLUXDB – Teknisk systemoversikt

3.1 Buckets

haos-oyna-raw

- ren rålogging fra MQTT

- liter/min

- total liters

- EM50 strøm data

- timestamp direkte fra pumpehus

haos-oyna-waterflow

- ferdig aggregerte data:

  - waterflow_minute

  - waterflow_hour

  - waterflow_day

haos-oyna-pressure

- virtuell trykkmodell

- pump runtimes

- cycles

- liters per cycle

haos-oyna-leakage

- leak_score

- baseline

- nightly profile

- long-term patterns

3.2 Measurements (strukturert)

Flow:

_waterflow

_fields:

- lpm

- total_liters

- pulses

Pumpe elektriske målinger:

_em50

_fields:

- voltage

- current

- active_power

- energy_total

Virtual pressure:

_pressure

_fields:

- virtual_bar

- cycle_liters

- cycle_runtime

Leakage:

_leak

_fields:

- leak_score

- baseline_runtime

- night_usage

3.3 Retention

Default retention (HA standard): forever
Kan justeres senere hvis datamengden blir stor.

🟫 4. KOMMUNIKASJONSKANALER (MQTT / API / NETTVERK)

4.1 MQTT Topics

Flow meter (Shelly 1 Gen4)

shelly/1g4/liters_per_minute

shelly/1g4/total_liters

shelly/1g4/events

Pumpe (EM50)

shelly/proem50/status/em1:0

shelly/proem50/status/switch:0

shelly/proem50/command/switch:0

4.2 HA API / NR websockets

- HA Websocket API tilgjengelig

- Node-RED HA Websocket Nodes: event state, call service, get entity

4.3 Nettverk

- WiFi: Ruckus R310

- Transport: MQTT over internett (TLS optional)

- Endpoint: haos-oyna.duckdns.org

- Reverse proxy: Nginx Proxy Manager

- Routed to HA (8123), Mosquitto (1883/8883)

🟧 5. SYSTEM STATE – Hvordan systemet fungerer akkurat nå

5.1 Styring

- P2 kan styres via:

  - mekanisk trykkbryter

  - gammelt kontrollskap (manual mode)

  - Shelly EM50 + ABB (AUTO mode)

5.2 Overvåkning

- Flow overvåkes 1:1 i HA og lagres i InfluxDB

- Stromforbruk overvåkes og brukes til:

  - cycle detection

  - overload detection

5.3 Analyse

- Node-RED beregner:

  - virtuelt trykk

  - lekkasje

  - sykluser

  - runtime

  - liters/cycle

  - frostfare

5.4 Digital twin status

- Systemet kan i dag:

  - predikere lekkasjer

  - predikere trykkfall

  - gi nattforbruksanalyse

  - foreslå tiltak

  - stoppe pumpe ved fare

🟦 6. AI-MODELL INPUT – Strukturert format

Dette er en “machine-readable” systemmodell:

{

"home_assistant": {

"entities": {

"flow": ["sensor.waterflow_lpm", "sensor.waterflow_total_liters"],

"pump_power": ["sensor.pressure_pump_voltage", "sensor.pressure_pump_current", "sensor.pressure_pump_active_power"],

"virtual": ["sensor.virtual_pressure_bar", "sensor.pump_cycle_liters", "sensor.leak_score"],

"controls": ["switch.pressure_pump_contactor"]

},

"input_helpers": ["input_number.virtual_pressure_cutin", "input_number.virtual_pressure_cutout"],

"integrations": ["mqtt", "shelly", "node_red", "influxdb"]

},

"node_red": {

"flows": ["waterflow_ingest", "cycle_detection", "virtual_pressure", "leakage", "safety_shutdown"],

"context": ["baseline", "pressure_state", "cycle_history"],

"mqtt_commands": ["p2_on", "p2_off"],

"functions": ["frost_detection", "pressure_model", "leak_score"]

},

"influxdb": {

"buckets": ["haos-oyna-raw", "haos-oyna-waterflow", "haos-oyna-pressure", "haos-oyna-leakage"],

"measurements": ["flow", "pressure", "leak", "power"]

},

"communication": {

"mqtt_topics": ["shelly/1g4/*", "shelly/proem50/*"],

"wifi": "ruckus_r310",

"endpoint": "haos-oyna.duckdns.org"

}

}